## HI
No. | Humidity [ppm] | Acidity [mg KOH/g] | Dielectric Strength [kV] | Dissipation factor [%] | Dissolved gases [ppm] | DP
1 | 22 | 0.07 | 52 | 0.14 | 671 | 603.4457
2 | 16.5 | 0.058 | 61 | 0.174 | 142.15 | 519.944
3 | 26 | 0.09 | 48 | 0.249 | 359 | 717.1429
4 | 9 | 0.08 | 49 | 0.1 | 2608 | 454.5491
5 | 42 | 0.22 | 46 | 0.221 | 2093 | 245.3491
6 | 10 | 0.09 | 62 | 0.733 | 1195 | 454.5491
7 | 21.2 | 0.349 | 33.5 | 0.257 | 366.1 | 160.0349
8 | 12.4 | 0.025 | 44.4 | 0 | 49 | 843.9136
9 | 12.5 | 0.065 | 56.2 | 0.101 | 49 | 937.0146
10 | 10.9 | 0.02 | 56.2 | 0 | 401 | 1002.857
11 | 7.1 | 0.008 | 50.4 | 0 | 59 | 1002.857
12 | 21 | 0.09 | 29 | 0.027 | 492 | 323.3
13 | 7 | 0.04 | 56 | 0.019 | 561 | 532.69
14 | 22 | 0.15 | 52 | 0.033 | 203 | 273.69
15 | 13 | 0.2 | 42 | 0.072 | 663 | 340.65

## FC
No. | Overload level | Mean Load (MVA) | Critical Loads | Oil Volume (L) | Proximity of other buildings (m) | Penalties (MVA) | Overload level | Numerical Value | Critical Loads | Numerical Value
1 | Overloads other units | 13 | No loads | 16850 | 382 | 30 | Produces unavailability and disconnections on the whole system | 0.9 | Several Loads | 0.85
2 | Produces unavailability and disconnections on the whole system | 14 | At least one load | 20700 | 42 | 40 | Overloads other units and produces unavailability | 0.7 | At least one load | 0.5
3 | Overloads other units and produces unavailability | 21 | Several loads | 40750 | 440 | 80 | Overloads other units | 0.5 | No loads | 0.15
4 | Overloads other units and produces unavailability | 26 | Several loads | 37150 | 394 | 80 | Occasionally overloads other units | 0.3
5 | Overloads other units and produces unavailability | 15 | Several loads | 6300 | 426 | 15 | No Overloads other units | 0.1
6 | Overloads other units and produces unavailability | 33 | Several loads | 36700 | 393 | 80
7 | Produces unavailability and disconnections on the whole system | 13 | At least one load | 28150 | 362 | 50
8 | Produces unavailability and disconnections on the whole system | 11 | No loads | 7200 | 92 | 15
9 | Occasionally overloads other units | 10 | No loads | 14600 | 427 | 20
10 | Produces unavailability and disconnections on the whole system | 44 | Several loads | 27700 | 254 | 60
11 | Overloads other units and produces unavailability | 13 | At least one load | 23400 | 422 | 40
12 | Overloads other units | 20.89 | Several loads | 16800 | 140 | 30
13 | Produces unavailability and disconnections on the whole system | 15.59 | Several loads | 17450 | 97 | 30
14 | Occasionally overloads other units | 7.69 | Several loads | 9800 | 97 | 15
15 | Overloads other units and produces unavailability | 16.65 | Several loads | 12300 | 140 | 30
No. | Overload level | Mean Load (MVA) | Critical Loads | Oil Volume (L) | Proximity of other buildings (m) | Penalties (MVA)
1 | 0.5 | 13 | 0.15 | 16850 | 382 | 30
2 | 0.9 | 14 | 0.5 | 20700 | 42 | 40
3 | 0.7 | 21 | 0.85 | 40750 | 440 | 80
4 | 0.7 | 26 | 0.85 | 37150 | 394 | 80
5 | 0.7 | 15 | 0.85 | 6300 | 426 | 15
6 | 0.7 | 33 | 0.85 | 36700 | 393 | 80
7 | 0.9 | 13 | 0.5 | 28150 | 362 | 50
8 | 0.9 | 11 | 0.15 | 7200 | 92 | 15
9 | 0.3 | 10 | 0.15 | 14600 | 427 | 20
10 | 0.9 | 44 | 0.85 | 27700 | 254 | 60
11 | 0.7 | 13 | 0.5 | 23400 | 422 | 40
12 | 0.5 | 20.89 | 0.85 | 16800 | 140 | 30
13 | 0.9 | 15.59 | 0.85 | 17450 | 97 | 30
14 | 0.3 | 7.69 | 0.85 | 9800 | 97 | 15
15 | 0.7 | 16.65 | 0.85 | 12300 | 140 | 30

## RI
No. | Health Index | Consequence Factor | Risk Index | HI*CF
1 | 0.427 | 0.438 | 0.5409 | 0.1869
2 | 0.3 | 0.687 | 0.4139 | 0.2062
3 | 0.338 | 0.562 | 0.459 | 0.1902
4 | 0.551 | 0.562 | 0.6715 | 0.3098
5 | 0.939 | 0.509 | 0.7192 | 0.4776
6 | 0.563 | 0.562 | 0.6748 | 0.3168
7 | 0.939 | 0.562 | 0.7194 | 0.5282
8 | 0.198 | 0.508 | 0.3221 | 0.1005
9 | 0.3 | 0.531 | 0.4122 | 0.1592
10 | 0.202 | 0.667 | 0.3227 | 0.1348
11 | 0.11 | 0.562 | 0.2776 | 0.0621
12 | 0.525 | 0.553 | 0.6657 | 0.2904
13 | 0.3 | 0.611 | 0.4249 | 0.1832
14 | 0.775 | 0.437 | 0.5699 | 0.3385
15 | 0.525 | 0.611 | 0.6665 | 0.3208

## Location
No. | Lat | Lon
1 | 12.5842 | -81.7035
2 | 12.5748 | -81.7118
3 | 12.5812 | -81.6957
4 | 12.5752 | -81.7198
5 | 12.5844 | -81.6946
6 | 12.5686 | -81.7147
7 | 12.5916 | -81.7067
8 | 12.5682 | -81.7229
9 | 12.5657 | -81.7157
10 | 12.5524 | -81.7216
11 | 12.5563 | -81.7061
12 | 12.5287 | -81.7113
13 | 12.553 | -81.7309
14 | 12.4983 | -81.7334
15 | 12.4962 | -81.7198